Specification for Dissolved Oxygen Meter w/ Flush

Class 1 Div 2

Application

Continuous on-line measurement of dissolved oxygen in water within the range of 0-20 mg/l for aeration basins and final effluent in municipal or industrial wastewater treatment plants.  Assembly to consist of one control box with one or two DO sensors and one or two flushing solenoid valves per attached spec.

Oxygen Electrodes – DO Sensor must be able to accept either electrode!

O2O Optical

The electrode must be a replaceable Optical type cartridge using blue and red LED lights to excite the luminophor film on the cartridge.  Electrode must use new Phase Shift technology with focusing lens to obtain larger measuring area and more stable measurement.  
A detector measures the amount of excited blue light and the red light is the zero of reference diode.  Temperature sensor must be built into the electrode to minimize instability due to temperature shifts.  Electrode must be designed to withstand mechanical flushing with 30 psig water or air and have 3grooves in electrode to match flushing nozzles to obtain good flushing of lense.  Electrode shall have protective UV film to alleviate damage from exposure to the sun light.  Measuring range shall be 0-20 mg/l.

OR

Clark Cell

The electrode must be a replaceable Clark type cartridge design with active materials of gold/silver (cathode/anode) that are treated to maximize their life span.  Electrode to have reliability error (1% and FEP (Teflon) membrane.  Electrode should be designed to operate 12-18 months at 3-5 mg/l operation between replacement and should not require recalibration more than once every 6 months.  The electrode must be “throw away” design -  rechargeable designs are not acceptable.  Temperature sensor must be built into the electrode to minimize instability due to temperature shifts.  The electrode body is to be made of PVC with SS membrane retaining ring and equipped with an o-ring seal.  Measuring range of 0-20 mg/l.

Sensor

Sensor housing to be 316SS with 33’ M12 extra heavy duty cable that meets or exceeds Class 1 Div. 2 requirements.  Cable to plug into control box and sensor to have built-in self identity logic so control box acknowledges sensors identity and calibration points which are stored in sensor’s memory.  Sensor must be able to accept either an Optical  electrode or Clark Cell membrane electrode without a design change.  Both should plug into the same connector and mount in the same installation hole.  Calibration of the both type electrodes by air calibration over a bucket of water to match saturated air solubility chart.  Sensor designed for 32 –122 F operating range.    Sensor housing to have three (3) SS  flushing nozzles which can be used if flushing solenoid valve is added to assembly.  Flushing media to be 30 psig compressed air or water depending on customers preference.

Signal Processor Control Box

Control box to support two sensors, which can be either/or dissolved oxygen, suspended solids,  pH, or open channel flow sensors and generate up to 4 independent and isolated 4-20 mA output signals.  Control box to be designed for future upgrade to commonly used fieldbus protocols by installing a protocol board.  Microprocessor based control box with self-instructing menu, digital circuitry, and illuminated graphical LCD display.  Graphical display to show solids concentrations in ppm, mg/l or % solids and 0-100% of mA output.  Graphical display to show calibration points and current suspended solids concentration.  The control box produces two linearized 4-20 mA, max 500 ohms galvanically isolated, output signals (12 bit resolution) proportional to suspended solids concentrations.  Light on front panel to indicate status of alarm.  To avoid fluctuating output signal, the control box should have a dampening feature or integration time, which can be set from 1 to 999 seconds.  The enclosure should be watertight molded polycarbonate box, NEMA 4X (IP65).  The power supply must be equipped with filter, fuse and varistors for protection against power surges.  The control box should have EEPROM memory.  Following a power failure the control box should start up and resume measuring without requiring recalibration.  Power supply is to be 110/1/60 or 220/1/50.  Control box to be equipped with built-in heater on circuit board to maintain proper temperature inside control box down to –20 F outside temperature.  Y-splitters are to be supplied for attachment of multiple digital sensors to a common control box.  Control box switching power supply must have current fold back protection and transit protection on power and communication loops to meet Class 1 Div. 2 requirements for NFPA 820, Fire Protection Code of 1999.

Programming Module

All programming and settings are performed from the outside of the control box by using a self-instructing menu controlled by three touch pad keys.  Calibration of the unit should be done against air.  If two oxygen electrodes are connected, then both should be able to be calibrated simultaneously.  Incorrect settings must not damage the unit. Special plug-in proms or manually adjustable potentiometers for programming are not acceptable.  Tamperproof programming feature is required to keep settings from being changed, except by authorized personnel.  In the event of power loss, an EEPROM memory should save programming during power outages rather than a battery backup.

Self-Diagnostics

The software should be of Multi-task design.  It should also contain a watch-dog function connected to the microprocessor.  The software should inform the “watch-dog” at least once per second that the device is working properly.  If it does not, then the “watch-dog” shall restart the processor in order for the unit to resume measuring.

Sensor Mounting  - Telescoping Rod Mounting

The sensor is to be attached to a telescoping fiberglass rod with a pvc sensor holder.  The rod

should be adjustable from 5’-13’.  Mounting bracket to be SS spring coil design for mounting

to 1.5” handrail, which will allow rod to move up and down without damage to rod.  PVC rod

holder to slip into spring mounting bracket assembly and should have SS retaining clip.  Rod to act as secondary protection of cable in Nema 7 areas.

# Control Box Mounting

Control box to be mounted to 1/8” aluminum mounting plate with rain lip and opaque sun shield,  SS hinge and SS u-bolts for mounting to handrail.  One or two flushing solenoid valves to be mounted to plate and prewired at factory to the control box as required.

Flushing of Sensor

Flushing solenoid valves to be mounted to mounting plate and prewired at factory to the control box.  Flushing liquid can be 30 psig plant water or reuse water that is filtered thru a 20 micron filter to alleviate flushing nozzle plugging.

Warranty

The manufacturer shall warrant the equipment to be free of defects from workmanship and material for a period of one (1) year after shipment.  Warranty for electrodes to be six (6) months.  Electrodes to ship one (1) week prior to start-up so customer gets fresh electrodes at start-up.

Supplier

Specification is written around equipment manufactured by Cerlic Controls, AB, Model – BB2/O2X,  Phone  404-256-3097 or Fax  404-256-3094

File: O2X Class 1 Div 2                                                                        JJ&G  Date 020217