Specification for pH/Redox Meter with Flush

Application

Continuous on-line measurement of pH or Redox for mounting in open channels, basins or tanks, with optional flushing system.  Measuring ranges of 0(14 for pH or -2000...+2000 mV for Redox potential for municipal and industrial wastewater treatment plants.

Electrode

The principle of measurement to be based on the measurement of pH and Redox as a function of millivolt.  pH electrodes should be non-refillable gel type made of glass containing measuring and reference electrodes, which in combination provide a voltage linear to the pH.  Electrode to have male type BNC connector for attachment to amplifier.  Refillable  electrodes are not acceptable.

Amplifier

The electrode should deliver a voltage, which is proportional to the pH or Redox value.  An amplifier is to be supplied to convert the pH & redox signals to RS485 output signals to a control box.  Amplifier to be supplied with 33’ (10 m) cable and M12 connector for attachment to the control box.  Cable can be lengthened with extension cables up to 165’ (50m).  Amplifier to have female BNC connector for attachment to pH or Redox electrodes.   Amplifier to be mounted in 39” long SS housing with optional flushing system.  Flushing media should be 40-60 psig air or water depending on customer’s preference.

Signal Processor Control Box

Control box to support two sensors, which can be either/or dissolved oxygen, suspended solids,  pH, ORP, or open channel flow sensors and generates up to 4 independent and isolated 4-20 mA output signals.  Control box to be designed for future upgrade to commonly used fieldbus protocols by installing a protocol board.  Microprocessor based control box with self-instructing menu, digital circuitry, and illuminated graphical LCD display.  Graphical display to show PH or Redox.    Alternate screen to show the date when the PH sensor was last calibrated (Redox does not require calibration).  The control box produces two linearized 4-20 mA, max 500 ohms galvanically isolated, output signals (12 bit resolution) proportional to pH or ORP.  Control box to have field adjustable contrast from front keyboard panel.  Light on front panel to indicate status of alarm.  To avoid fluctuating output signal, the control box should have a dampening feature or integration time, which can be set from 1 to 999 seconds.  The enclosure should be watertight molded polycarbonate box, NEMA 4X (IP65).  The power supply must be equipped with filter, fuse and varistors for protection against power surges.  The control box should have EEPROM memory, so that following a power failure the control box should start up and resume measuring without requiring recalibration.  Power supply is to be 110/1/60 or 220/1/50.  Control box to be equipped with built-in heater on circuit board to maintain proper temperature inside control box down to –20 F outside temperature.  Y-splitters are to be supplied for attachment of multiple digital sensors to a common control box.

Programming Module

All programming and settings are performed from the outside of the transmitter by using a self-instructing menu controlled by three touch pad keys.  Special plug-in proms or manually adjustable potentiometers for programming are not acceptable.  Tamperproof programming feature is required to keep settings from being changed, except by authorized personnel.  In the event of power loss, an EEPROM memory should save programming during power outages rather than a battery backup.

The transmitter should have  “smart” and manual calibration features.  “Smart” calibration means that the unit automatically recognizes the pH value of three different buffer solutions.  Buffer solutions for “smart” calibration should be pH values of 4,7 or 10.  When pH calibration is complete, then condition of electrode is to be presented on display as a slope expressed in %.  When performing a manual calibration, pH values of buffer solutions should be entered manually.

ORP control box shall offer a one point mV calibration option. ORP shall be calibrated to 200 mV, 400 mV or 600 mV buffer solution depending on which is closest to actual operating conditions.

Flushing program to include independent cleaning function settings for each channel with three (3) programmed functions: 1) intervals from 10 minutes to 99,999 minutes, 2) length of cleaning between 1-99,999 seconds and 3) recovery after cleaning  from 1 to 99,999 seconds.  Output signal should be frozen during cleaning and recovery cycles at initial value so connected equipment will not receive a false pH or Redox readings.

Self-Diagnostics

The software should be of Multi-task design.  It should also contain a watch-dog function connected to the microprocessor.  The software should inform the “watch-dog” at least once per second that the device is working properly.  If it does not, then the “watch-dog” shall restart the processor in order for the unit to resume measuring.

Sensor Mounting

1. SS Slide Rail   - Sensor to be supplied with SS slide rail (20” long) and two (2) SS sensor

clips.  The slide rail is to be attached to wall or mounting plate with SS anchors by

contractor.  The amplifier and electrode are to be installed in 1” ( 316SS rod housing by 39”

long for insertion in SS clips.

2. PVC Clip attachment to O2X & ITX sensors - Electrode to be immersion design with 30’

cable for attachment to amplifier.  Electrode to be flush design and supplied with PVC clip

for attachment to side of Stainless Steel DO or Suspended solids sensor.  Amplifier to be

mounted to side of control box mounting plate.

3. Chain w/ SS Weight - Sensor to be supplied with 1 ¼” Ø aluminum rod L shaped, PVC rod

holder with SS spring coil mounting bracket for 1 ½” handrail attachment, 316 SS chain

(length as req’d), SS Sensor weight (8#) and pvc snap clips for attachment of submersible

electrodes.

4. Rod Mounting – The sensor is to be attached to a fiberglass telescoping rod with a pvc

sensor holder.  The rod should be adjustable from 5’ – 13’.  Mounting bracket to be 316SS

spring coil design for mounting to 1.5” aluminum handrail, which will allow the rod to

move in 2 directions with damage to the rod.  PVC rod holder to slip into spring mounting

bracket assembly an should have SS retaining clip.

Control Box Mounting

Control box to be mounted to 1/8” aluminum mounting plate with rain lip and opaqye sun shield, SS hinge and SS bolts u-bolts for mounting to handrail.  One or two flushing solenoid valves to be mounted to plate and prewired at factory to the control box as required.

Flushing

Electrode housing to be supplied with flushing nozzle and 5/16” black UV flushing hose.  Flushing solenoid valves to be mounted to control box mounting plate and prewired at factory.  Flushing liquid can be 30-40 psig plant water or reuse water that is filtered thru a 20 micron filter to alleviate flushing nozzle plugging.  Flushing can also be with 30-40 psig compressed air.

Warranty

The manufacturer shall warrant the equipment to be free of defects from workmanship and material for a period of one (1) year after shipment.  Warranty for electrodes to be six (6) months.

Supplier

Specification  is  written  around  equipment  manufactured  by  Cerlic  Controls,  AB,         Model – PHX/REX/BB2,   Phone  404-256-3097  or  Fax  404-256-3094 or approved equal by engineer prior to bid opening.

File: SPEC/pHX.DOC                                                                                               09/13    rev. 4